{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Rectas aplicadas"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":0,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Rectas aplicadas","index":0,"n_rows":65,"n_cols":17,"rows_kept":65,"cut":false,"hidden":false,"merged":[[6,15,7,15],[59,4,60,4],[57,1,57,4],[59,2,60,2],[59,3,60,3],[30,2,30,4],[33,2,33,4],[27,2,27,4],[39,2,39,4],[10,15,11,15],[12,15,14,15],[1,1,1,4],[21,2,21,4],[23,2,23,4],[36,2,36,4],[42,2,42,4]]}
[]
[null,"Superacions enregistrades 2022"]
[]
[null,"BW1","horàries >  200% VLE ","diàries  > 110% VLE","mensuals  >   VLE",null,null,null,"Funcions de calibració"]
[null,"SO2",0,0,0,null,null,null,null,null,null,null,"Rectes anteriors",null,null,"Informe en detall d'indisponiblitats i superacions:"]
[null,"NOx",0,0,0,null,"Grup","Contaminant","Pendent","Offset","Informe","Aplicació","Pendent","Offset",null,"BW1","Indisponiblitat el 18/06 a tots els contaminants (NOx, CO, SO2 i PST) per fall d'equip."]
[null,"Par",0,0,0,null,"BW1","CO",0.98,2.72,"2022-09-12","2022-10-06",0.78,18.32,null,"BW2","Indisponiblitat el 07 i 08/06 en el multiparamètric (NOx, CO, SO2) per fall d'equip."]
[null,"CO",0,0,0,null,"BW1","NOx",1.1200000000000001,0,"2022-09-12","2022-10-06",1.05,0,null,null,"Indisponiblitat el 18/06 a tots els contaminants (NOx, CO, SO2 i PST) per fall d'equip."]
[null,null,null,null,null,null,"BW1","SO2",1,-16,"2022-09-12","2022-10-06",0.8,0,null,"BW3","Indisponiblitat el 18/06 a tots els contaminants (NOx, CO, SO2 i PST) per fall d'equip."]
[null,"BW2","horàries >  200% VLE ","diàries  > 110% VLE","mensuals  >   VLE",null,"BW1","Partículas",521.86,0,"2022-09-12","2022-10-06",121.33,12.93,null,"TG3A","Superació horaria del 200% del VLE de Nox (90 mg/Nm3) el 18/11 degut a problemes d'injecció d'aigua."]
[null,"SO2",0,0,0,null,"BW2","CO",1.1299999999999999,14.32,"2022-08-26","2022-10-06",0.98,6.07,null,"TG3B","Superació horaria del 200% del VLE de NOx (90 mg/Nm3) el 12/07 degut a problemes d'injecció d'aigua. "]
[null,"NOx",0,0,0,null,"BW2","NOx",1.26,0,"2022-08-26","2022-10-06",1.07,0,null,null,"Superació horaria del 200% del VLE de NOx (90 mg/Nm3) el 25/08 degut a problemes d'injecció d'aigua. "]
[null,"Par",0,0,0,null,"BW2","SO2",1.03,-19.57,"2022-08-26","2022-10-06",0.85,0,null,"TG4A","Superació horaria del 200% del VLE de NOx (90 mg/Nm3) el 21/02 degut a problemes d'injecció d'aigua. "]
[null,"CO",0,0,0,null,"BW2","Partículas",544.66,0,"2022-08-26","2022-10-06",166.69,16.559999999999999,null,null,"Superació horaria del 200% del VLE de NOx (90 mg/Nm3) el 11/08 degut a problemes d'injecció d'aigua. "]
[null,null,null,null,null,null,"BW3","CO",1.1200000000000001,5.46,"2022-08-25","2022-10-06",0.91,11.2,null,null,"Indisponiblitat el 21/11 al SAM d' NOx i CO per fall d'equip."]
[null,"BW3","horàries >  200% VLE ","diàries  > 110% VLE","mensuals  >   VLE",null,"BW3","NOx",0.83,0,"2022-08-25","2022-10-06",0.86,0,null,"TG5A","Superació horaria del 200% del VLE de NOx (90 mg/Nm3) el 21/01 degut a problemes d'injecció d'aigua. "]
[null,"SO2",0,0,0,null,"BW3","SO2",0.99,5.56,"2022-08-25","2022-10-06",1.04,0]
[null,"NOx",0,0,0,null,"BW3","Partículas",96.91,0,"2022-08-25","2022-10-06",331.6,0]
[null,"Par",0,0,0,null,null,null,null,null,null,null,"Rectes anteriors"]
[null,"CO",0,0,0,null,"Grup","Contaminant","Pendent","Offset","Informe","Aplicació","Pendent","Offset"]
[null,null,null,null,null,null,"TG4A","NOx",0.96,0,"2022-01-19","2021-10-15",0.88,5.49]
[null,"TG1","Hores anuals funcionament < 500",null,null,null,"TG4A","Partícules",8.7100000000000009,0.18,"2022-01-19","2021-10-15",66.66,0]
[null,null,null,null,null,null,"TG4A","CO",1.01,-0.66,"2022-01-19","2021-10-15",0.95,5.28]
[null,"TG2","Hores anuals funcionament < 500",null,null,null,"TG4B","NOx",1.04,0,"2022-01-19","2021-10-12",0.99,0]
[null,null,null,null,null,null,"TG4B","Partículas",4.6399999999999997,0,"2022-01-19","2021-10-12",33.6,-2.9]
[null,null,null,null,null,null,"TG4B","CO",1.01,0.01,"2022-01-19","2021-10-12",1.1599999999999999,3.84]
[null,"TG3","horàries >  200% VLE ","diàries  > 110% VLE","mensuals  >   VLE",null,"TG5A","NOx",0.96,0,"2022-01-19","2021-10-19",1.35,-33.19]
[null,"SO2","Exenta de mesura",null,null,null,"TG5A","CO",0.96,0,"2022-01-19","2021-10-19",1.05,4.13]
[null,"NOx",3,0,0,null,"TG5A","Partículas",49.69,0,"2021-09-22","2021-11-22",296.39999999999998,0]
[null,"Par",0,0,0,null,"TG5B","NOx",1,0,"2022-01-19","2021-10-20",0.79,0]
[null,"CO","Valors vàlids molt inferiors a VLE",null,null,null,"TG5B","CO",1.21,0.04,"2022-01-19","2021-10-20",1.1499999999999999,4.3]
[null,null,null,null,null,null,"TG5B","Partículas",7.15,0,"2022-01-19","2021-10-20",11.5,0]
[null,"TG4","horàries >  200% VLE ","diàries  > 110% VLE","mensuals  >   VLE",null,"TG3A","SO2",0.95,3.06,"2018-04-03","2018-04-17"]
[null,"SO2","Exenta de mesura",null,null,null,"TG3A","NOx",1.01,0,"2020-04-23","2020-05-08",1.07,2.89]
[null,"NOx",2,0,0,null,"TG3A","Partícules",0.01,0,"2022-03-31","2022-07-18",12.92,0]
[null,"Par",0,0,0,null,"TG3A","CO",0.94,7.46,"2020-04-23","2020-05-08",1.03,1.64]
[null,"CO","Valors vàlids molt inferiors a VLE",null,null,null,"TG3B","SO2",0.96,1.85,"2018-04-03","2018-04-17"]
[null,null,null,null,null,null,"TG3B","NOx",0.88,7.34,"2020-03-30","2020-05-20",1.01,6.05]
[null,"TG5","horàries >  200% VLE ","diàries  > 110% VLE","mensuals  >   VLE",null,"TG3B","Partícules",14.64,0,"2020-03-30","2020-05-20",6.25,0]
[null,"SO2","Exenta de mesura",null,null,null,"TG3B","CO",0.99,1.86,"2020-03-30","2020-05-20",1,0.82]
[null,"NOx",1,0,0]
[null,"Par",0,0,0]
[null,"CO","Valors vàlids molt inferiors a VLE"]
[]
[null,null,"Hores de funcionament 2022"]
[]
[null,null,"Gener","Febrer","Març","Abril","Maig","Juny","Juliol","Agost","Setembre","Octubre","Novembre","Desembre",2022]
[null,"BW-1",744,672,721.4,720,576.97,720,430.52,525.48,0,0,1.02,2.5299999999999998,{"$f":"SUM(C48:N48)","v":5113.9199999999992}]
[null,"BW-2",725.12,488.23,743,720,652.85,673.52,699.98,744,0,0,1.33,1.28,5449.3099999999995]
[null,"BW-3",736.87,672,189.13,720,605.72,720,305.88,492.33,158,0,0,1,4600.93]
[null,"TG-1",33.25,0,0,7.22,8.2799999999999994,10,2.4,10.029999999999999,20.62,43.08,0,332.62,467.5]
[null,"TG-2",0,8.3800000000000008,8.4,7.62,3.45,9.98,2.83,0,0,8.93,4.0999999999999996,137.68,191.37]
[null,"TG-3",29.74,84.73,142.49,56.58,43.97,150.15,318.27,354.63,396.89,179.57,210.43,182.62,2150.0699999999997]
[null,"TG-4",164.59,158.97,287.73,193.17,301.27,243.74,581.46,526.28,530.13,508.73,320.68,227.77,4044.52]
[null,"TG-5",76.739999999999995,42.83,29.55,14.43,193.26,246.12,360.88,493.16,487.64,397.48,342.48,183.22,2867.79]
[]
[null,null,null,null,null,null,null,null,null,null," "]
[null,"Hores acumulades TG's"]
[]
[null,null,"Hores acumulades 20-10-13 - 31-12-21","Hores acumulades 2022","Hores restants fins arribar a 10.000 h"]
[]
[]
[null,"TG1",{"$f":"1192.54+110.85+165.3+403","v":1871.6899999999998},{"$f":"O51","v":467.5},{"$f":"10000-(C63+D63)","v":7660.81}]
[]
[null,"TG2",{"$f":"2096.18+629.38+150.7+329","v":3205.2599999999998},{"$f":"O52","v":191.37},{"$f":"10000-(C65+D65)","v":6603.3700000000008}]